# BESS Benchmarks in India: What They Are and How to Read Them

Status as of 23 October 2026

# Simple Way to Think About It

A grid battery is like a warehouse for electricity that the DISCOM rents. The developer builds it and the DISCOM pays a fixed monthly rent to use it. Every benchmark is either about how good the warehouse is (technical) or about the rent and build cost (commercial).

# 1. Size: MW vs MWh

MW = how fast the battery can push power out (width of the warehouse door).

MWh = how much energy it holds (warehouse volume).

Duration = MWh / MW. A 1 MW / 2 MWh battery runs at full power for 2 hours. 2-hour systems cover the evening peak; 4-hour systems cover a longer one.

# 2. Technical Benchmarks in Tenders

Example: SECI 50 MW / 100 MWh standalone ESS tender, August 2026.

| Benchmark | Requirement | Meaning | Penalty if missed |
| --- | --- | --- | --- |
| Round-trip efficiency (RTE) | >= 85% AC-to-AC, monthly | Put 100 units in, at least 85 must come out | Rs 3.50/kWh on extra losses; full monthly tariff withheld if below 70% |
| Availability | >= 95% annual | Battery ready to use 95% of the time | 2x capacity charge for unavailable capacity |
| Cycles | 1-2 per day; max 485 in contract period | One cycle = one full charge and discharge | - |
| Duration | Mostly 2-hour; shift towards 4-hour | Hours of full-power discharge | - |
| Co-located storage (CEA advisory) | >= 10% of solar capacity, >= 2 hours | Advisory, not mandatory | - |
| Domestic content | >= 20% of procurement cost | Needed to qualify for VGF | No VGF |

# 3. Tariff Benchmarks (Rs lakh per MW per month)

This is the rent. It is paid for capacity, not energy. The DISCOM pays it whether or not it uses the battery, and supplies its own power for charging.

| Duration | Tender | Discovered tariff |
| --- | --- | --- |
| 2-hour | GUVNL 335 MW / 670 MWh (Feb 2026) | 2.10 |
| 2-hour | GUVNL 450 MW / 900 MWh (Aug 2026) | 2.32 |
| 4-hour | WBSEDCL 250 MW / 1,000 MWh (Jan 2026) | 3.47 |
| 4-hour | WBSEDCL 500 MW / 2,000 MWh (Aug 2026) | 4.35-4.39 |
| 2-hour (record low) | RVUNL 1 GW / 2 GWh (Oct 2025) | 1.775 |

Tariffs have risen through 2026 after very low 2025 bids, which raised viability concerns.

# 4. Cost Benchmarks (August 2026)

| Item | Benchmark |
| --- | --- |
| 314 Ah LFP cell, China (after tax) | ~USD 54/kWh (~Rs 5,114/kWh) |
| LFP cell, landed India | ~USD 61-66/kWh (~Rs 5,824-6,301/kWh); 14-23% above China |
| 2-hour AC container system, China | ~USD 86/kWh (~Rs 8,239/kWh) |
| Installed, India, 10 MWh+ | ~Rs 15,000-20,000/kWh |
| Installed, India, small C&I (100-500 kWh) | ~Rs 30,000-40,000/kWh |
| VGF support (tranche 2) | Rs 18 lakh/MWh |

The cell is about 60% of the container price, which is why local cell manufacturing and the 20% domestic content rule matter for BESS economics.

# 5. Worked Example (Own Rough Calculation)

These are illustrative calculations from the benchmarks above, not figures from a report. Assumes 1 cycle per day.

2-hour at Rs 2.10 lakh/MW/month: 1 MW x 2 h x 30 days = 60 MWh shifted per month, so about Rs 3.5 per kWh shifted.

4-hour at Rs 4.35 lakh/MW/month: 120 MWh shifted per month, so about Rs 3.6 per kWh shifted.

This is the cost of moving midday solar to the evening peak, on top of the charging power and ~15% loss.

Capex for 1 MW / 2 MWh utility project: ~Rs 2.5-3 crore (containers ~Rs 8,200/kWh plus civil, grid connection and balance of system).

VGF reduces capex by ~Rs 36 lakh (Rs 18 lakh/MWh x 2 MWh).

Rent income: Rs 2.10 lakh x 12 = ~Rs 25 lakh per year.

Payback: roughly 9-10 years before O&M, interest and battery replacement. This is why record-low 2025 bids were seen as risky.

# Sources

1. IEEFA-JMK EnergyWatts, September 2026 - https://ieefa.org/sites/default/files/2026-09/ESSjmk-0926.pdf

2. SolarQuarter - SECI invites bids for 50 MW / 100 MWh standalone ESS (Aug 2026) - https://solarquarter.com/2026/08/29/seci-invites-bids-for-50-mw-100-mwh-standalone-energy-storage-system/

3. SolarQuarter - RVUNL concludes 1 GW / 2 GWh BESS auction at record low Rs 1.775 - https://solarquarter.com/2025/10/08/rvunl-concludes-1-gw-2-gwh-bess-auction-with-record-low-tariff-of-₹1-775

4. pv magazine India - 10.4 GW standalone BESS awarded in 2025, tariff viability concern (IEEFA-JMK) - https://www.pv-magazine-india.com/2026/05/19/india-awards-10-4-gw-of-standalone-bess-capacity-in-2025-but-tariff-viability-remains-a-concern-ieefa-jmk-report/

5. DC&T Global - BESS in India: 2026 C&I buyer's guide - https://www.dcntglobal.com/bess-india-2026-a-ci-buyers-guide/

6. Energy-Storage.news - 20% domestic content rule for BESS VGF - https://www.energy-storage.news/?p=92648

7. SolarQuarter - Rs 5,400 crore VGF and transmission incentives (CEA advisory) - https://solarquarter.com/2026/08/12/india-strengthens-energy-storage-framework-with-inr-5400-crore-vgf-and-transmission-incentives/

8. SolarQuarter - Govt roadmap for 60.63 GW storage by FY30 (VGF rates) - https://solarquarter.com/2026/02/04/government-unveils-multi-pronged-policy-financial-and-regulatory-roadmap-to-build-60-63-gw-energy-storage-capacity-by-fy30/