## Slide 1: BESS in India: demand, government target and present situation
Government wants 41.65 GW of BESS by FY30; about 9.6 GWh is operating today, against ~151 GWh already tendered
Government targets and support
Item | Detail
CEA target, FY2029-30 | 60.63 GW storage: 41.65 GW BESS + 18.98 GW pumped storage (PSP)
National Electricity Plan, FY2031-32 | ~73.9 GW (47.2 GW BESS + 26.7 GW PSP), ~411 GWh
Energy Storage Obligation (MoP) | 1% of consumption in 2023-24 rising to 4% by 2029-30; ≥85% of stored energy must be renewable
VGF tranche 1 (Mar 2024) | ₹3,760 cr for 13.2 GWh at ₹27 lakh/MWh
VGF tranche 2 (Jun 2025) | ₹5,400 cr from PSDF for 30 GWh at ₹18 lakh/MWh
ISTS charge waiver | 100% for co-located BESS commissioned by Jun 2028; falls 25% a year after that
Domestic content (Dec 2025) | ≥20% of BESS procurement cost must be local to get VGF; EMS software counts
CEA co-location advisory | New solar to add storage ≥10% of capacity, ≥2 hours (advisory, not mandatory)
Manufacturing | 10 GWh of ACC PLI earmarked for grid storage; Budget 2026-27 duty exemption on cell machinery
Demand outlook (storage requirement)
Source | Horizon | Requirement
CEA (Optimal Generation Mix) | FY2029-30 | 41.65 GW BESS
Rubix Data Sciences | FY2031-32 | ~236 GWh BESS (≈7× today)
National Electricity Plan (CareEdge) | FY2031-32 | ~411 GWh (BESS + PSP)
IESA | 2035-36 | ~888 GWh total storage
Present situation (Oct 2026)
Metric | Figure
Installed BESS, Dec 2025 | ~0.78 GWh
Installed BESS, H1 2026 | ~8.7 GWh (8.2 GWh added in H1 2026)
Operational BESS, Aug 2026 | ~9.6 GWh (mostly merchant projects)
Expected by end-2026 | >10 GWh
BESS tendered by Aug 2026 | ~151 GWh (+ ~142 GWh PSP)
Cumulative tender pipeline | ~260 GWh
Awarded storage pipeline | ~54 GW
Source: [1] SolarQuarter (CEA roadmap, Feb 2026); [2] SolarQuarter (VGF, Aug 2026); [3] CareEdge via ANI; [5] Rubix via pv magazine India; [6] IESA via Angel One; [7] Mercom via ESS News; [8] IEEFA-JMK EnergyWatts Sep 2026; [10] JMK EnergyWatts Sep 2026; [14] Renewable Watch (ESO); [15] Energy-Storage.news (20% DCR)

## Slide 2: Why BESS is required: solar peaks at noon, demand peaks after sunset
India keeps adding solar and wind, but without storage the extra midday power is curtailed and the evening peak still needs coal
The problem
Issue | Evidence
Time mismatch | Solar output peaks around midday; peak demand comes in the evening after sunset
Capacity vs generation | Non-fossil ≈50% of installed capacity but only ≈29% of generation
Steeper duck curve | Morning ramp-down 28 GW (May 2025) → 50 GW (May 2026); evening ramp-up 68 → 80 GW
Solar wasted | ~8.1 TWh solar curtailed in Q1 FY27; Jul-Aug 2026: 1,462 MU solar + 373 MU wind curtailed while peak demand hit 270 GW
Why it is wasted | At midday supply exceeds demand and grid limits bite; with no storage the grid operator backs RE down
Storage today | ~9.6 GWh operational; meets only 1-2% of night-time peak
Why no other solution fills the gap
Option | Limitation
Coal plants | Ramp slowly and cannot go below ~55% minimum load; add emissions
Gas peakers | Little domestic gas; imported LNG is costly
Pumped hydro | Good for long duration but site-specific, 5-8 years to build; runs alongside BESS (18.98 GW target)
More transmission | Moves power between regions, but cannot move noon power to night
Demand response | Helpful but small scale today
BESS | Responds in under a second, built in ~18 months, sits at substations or solar parks
Solar and wind growth (GW, cumulative)
As of | Solar | Wind | Solar + wind
Mar 2022 | 54.0 | 40.4 | 94.4
Mar 2023 | 66.8 | 42.6 | 109.4
Mar 2024 | 81.8 | 45.9 | 127.7
Mar 2025 | 105.6 | 50.0 | 155.6
Mar 2026 | 150.3 | ~56 | ~206
Sep 2026 | 171.1 | 59.2 | 230.3
FY2026: record 44.6 GW solar (+87% YoY) and 6 GW wind added.
H1 FY27: 20.8 GW solar and 3.1 GW wind added.
Solar has roughly tripled in 4.5 years; wind grew ~1.5×.
Mar 2026 wind is derived (Mar 2025 + 6 GW added).
Source: [3] CareEdge via ANI (ramp, gen share); [4] TaiyangNews/CREA (curtailment); [8] IEEFA-JMK EnergyWatts Sep 2026; [11] Energetica India (Sep 2026 capacity); [12] JMK via pv magazine India (FY2026); [13] MNRE year-end physical progress; [1] SolarQuarter (PSP target)

## Slide 3: BESS manufacturers: global leaders and Indian capacity
Global supply is concentrated in China; India has ~60 GWh of pack/container assembly but only ~2.5 GWh of operating cell capacity
Global top 5 BESS cell suppliers (2025)
Rank | Company | HQ | Share of 2025 BESS cells
1 | CATL | China | ~20% (29% in 2024)
2 | HiTHIUM | China | ~12%
3 | EVE Energy | China | ~12%
4 | BYD | China | Not disclosed
5 | CALB | China | Not disclosed
612 GWh of BESS cells shipped in 2025 (+95%); top 10 held ~89%, all Chinese.
Global top 5 BESS system integrators (2025)
Rank | Company | HQ | Note
1 | Tesla (Megapack) | US | #1 for 3rd year (Wood Mackenzie); 46.7 GWh deployed
2 | Sungrow | China | #2 (Wood Mackenzie); #3 by shipments
3 | BYD | China | #3 (Wood Mackenzie); #1 by shipments (Benchmark)
4 | Fluence | US | One of two non-Chinese top-10 integrators
5 | Huawei | China | Regional leader in Europe
Top 3 integrators held ~30% of the market; Chinese integrators 76%. Ranks 4-5 are not published as a global ranking.
India: top 5 BESS (pack / container) manufacturers by capacity
Company | Location | Capacity | Status | Share of India pack capacity*
Tata AutoComp–Gotion JV | Pune, Maharashtra | 6 GWh (full ramp) | Supplying Tata Power projects | ~10%
Waaree ESS | Gujarat | 5.15 GWh (target 20 GWh) | Commissioned Jul 2026 | ~9%
JSW Energy | Pune, Maharashtra | 5 GWh | Commissioned Q4 FY26 | ~8%
Pace Digitek (Lineage Power) | Bidadi, Karnataka | 5 GWh (10 GWh by end-FY27) | 1.25 GWh built in first year | ~8%
iNVERGY | Dasna, Uttar Pradesh | 3 GWh | Inaugurated (₹200 cr) | ~5%
*Own calculation: nameplate capacity ÷ ~60 GWh national pack capacity (IEEFA). Also: Voltters 3 GWh (MP); planned Premier 6 GWh, VSL PowerHive 7.5 GWh, Powertrac 10 GWh, Neuron 5 GWh. Cells: Ola 2.5 GWh is the only operating cell plant, so most BESS cells are imported from China.
Source: [16] Benchmark Mineral Intelligence; [17] Wood Mackenzie via SolarQuarter; [18] InfoLink via ESS News; [20] Energetica India; [21] Renewable Watch (Waaree); [22] ESS News (Pace); [23] pv magazine India (JSW); [24] Energy-Storage.news (Tata AutoComp); [9] IEEFA-JMK Jun 2026; [8] IEEFA-JMK Sep 2026

## Slide 4: Basic structure of a BESS: from cell to grid
Energy flows left to right on charge-discharge; BMS, EMS and SCADA control it, while cooling and fire systems keep it safe
Cell
LFP, 3.2 V, ~1 kWh (314 Ah)
Module
16 cells in series, ~51 V, ~16 kWh
Rack
~400 cells, ~1,280 V DC, rack BMS
Container
~5 MWh: racks + cooling + fire system
PCS
Inverter: DC ↔ AC, controls P & Q
Transformer
Steps up LV to 11-33 kV
Switchgear & meter
Isolates faults, measures energy
Grid
STU / ISTS substation
DC side
AC side
BMS: Watches every cell: V, I, temperature, SOC/SOH; trips contactors
EMS: Decides when and how much to charge or discharge
SCADA / grid operator (SLDC): Sends schedules, monitors plant
Control layer (dashed): signals, not power. Safety trips are hard-wired so they work even if communication fails.
Main components
Component | What it does | India supply status
Battery cells (LFP) | Store the energy; about 60% of container price | Mostly imported from China; Indian lines just starting
BMS | Protects cells, balances them, estimates SOC/SOH | Mostly comes with imported battery systems
PCS / inverter | Converts DC↔AC; grid-forming and black start required for ≥50 MW from Apr 2027 | Global makers with Indian plants (Sungrow, Delta, Hitachi Energy)
Thermal management | Keeps cells in a narrow temperature band (liquid cooling) | Containers and HVAC local; chillers often imported
Fire and explosion safety | Gas/smoke detection, suppression in every container, venting | Available locally; mandatory under CEA rules from Apr 2027
Transformer & switchgear | Step up voltage, isolate faults, protection relays | Strong Indian manufacturing base
EMS / SCADA | Dispatch decisions, monitoring, reporting to SLDC | Indian developers; EMS counts toward 20% domestic content
Source: [54] BESS Deep Research Report (ev repo, sections 3.3 and 4.3); [8] IEEFA-JMK Sep 2026 (cell share of container price); [36] Energetica India (CEA safety rules 2026); [37] SolarQuarter (CEA technical standards 2026); [15] Energy-Storage.news (20% DCR)

## Slide 5: BESS technologies compared
LFP is about 90% of new lithium-ion storage; other chemistries fill niches (cold climate, very long duration, lithium-free supply)
Parameter | LFP | NMC | LTO | Sodium-ion | Vanadium flow (VRFB)
Nominal cell voltage | 3.2 V | 3.6-3.7 V | 2.3-2.4 V | ~2.8-3.2 V | ~1.26 V
Energy density (Wh/kg) | ~160-205 | ~200-280 | ~60-90 | ~100-175 (claims) | ~15-25 (electrolyte)
Cycle life | 6,000-10,000+ | 2,000-5,000 | 10,000-20,000+ | ~3,000-6,000 (claims) | >15,000
System round-trip efficiency (AC) | ~85-90% | ~85-90% | ~85-90% | ~80-88% | ~65-75%
Thermal safety | High | Medium-low | Very high | High | Non-flammable
Low-temperature charging | Poor below 0 °C | Moderate | Excellent | Good | Good
Critical materials | Lithium, graphite | Li, nickel, cobalt, graphite | Lithium, titanium | Sodium, hard carbon | Vanadium
Cost position (2026) | Lowest Li-ion | Higher | Highest Li-ion | Close to LFP, falling | High capex; cheap extra hours
Best fit | 2-4 h grid peak shifting | Space-constrained sites | Fast frequency response, cold sites | Lithium-free, cold climates | 8 h+ long duration, high cycling
Status for grid storage | Dominant | Legacy / niche | Niche | Early commercial (CATL mass production 2026) | Commercial niche (175 MW / 700 MWh in China)
Share of BESS production | ~90% of 2025 Li-ion storage additions | Part of remaining ~10% | Part of remaining ~10% | Small; not reported separately (60 GWh CATL storage order) | Small; not reported separately
2025 production snapshot
Global storage additions 2025 | BESS cells shipped 2025 | Utility-scale vs small-scale cells | Supplier concentration
112 GW / 307 GWh (+48%); China 54%, US 16% | 612 GWh (+95%) | 557 GWh utility (~91%); 56 GWh small-scale (~9%) | Top 10 cell makers ~89%, all Chinese
Source: [54] BESS Deep Research Report (ev repo, section 6.7; typical datasheet values); [19] BloombergNEF via pv magazine USA (LFP 90%, 2025 additions); [18] InfoLink via ESS News (cell shipments); [16] Benchmark Mineral Intelligence

## Slide 6: LFP chemistry: how a lithium iron phosphate cell works
Lithium ions shuttle between graphite and iron phosphate through the electrolyte; electrons take the outside wire and do the work
Separator
Graphite
(−)
LiFePO₄
(+)
Electrolyte
Li⁺
Li⁺
Li⁺
Discharge: Li⁺ moves anode → cathode, e⁻ flow through the load; on charge both reverse
Load / grid
e⁻ →
Copper foil
Anode
Cathode
Aluminium foil
Cell sits in an aluminium prismatic can with a safety vent (not shown)
Reactions
Step | Reaction
Discharge, cathode | FePO₄ + Li⁺ + e⁻ → LiFePO₄ (Fe³⁺ → Fe²⁺)
Discharge, anode | LiC₆ → 6C + Li⁺ + e⁻
Overall | LiC₆ + FePO₄ ⇌ 6C + LiFePO₄
Mechanism | Intercalation: Li slides into the crystal without breaking it, so cells last thousands of cycles
Key properties
Property | LFP value
Voltage | 3.2 V nominal (2.5-3.65 V window)
Energy density | ~160-205 Wh/kg at cell level
Cycle life | 6,000-10,000+ cycles (stationary cells)
Safety | P-O bonds hold oxygen; thermal runaway starts ~270 °C vs ~210 °C for NMC
Cell size trend | 280 Ah → 314 Ah (~1 kWh) → 587-628 Ah (2025-26)
Weak points | Charging below 0 °C; flat voltage makes SOC hard to read
Materials | No nickel or cobalt: lithium, iron, phosphate, graphite
Source: [54] BESS Deep Research Report (ev repo, sections 5 and 6.1); [47] pv magazine (314 Ah → 500 Ah+ LFP cells, Jan 2026); [55] EV SIM.pptx, Generation 3 slide (thermal runaway temperatures)

## Slide 7: LFP cell components, materials and Indian suppliers
Cathode and anode are ~65% of cell cost and >90% are processed in China; India has started on cathode, anode, electrolyte and aluminium foil
Component | Material | Approx. per kWh* | Indian companies | Capacity / status
Cathode (CAM) | LiFePO₄ from lithium carbonate + iron phosphate | ~2 kg LFP; ~0.5-0.6 kg Li₂CO₃ | Himadri, GFCL EV, Altmin, Epsilon | Himadri 2,000 t by Dec 2026 → 40,000 t FY28; GFCL sales H2 FY27; lithium fully imported
Anode | Synthetic / natural graphite | ~1-1.2 kg | Epsilon, Himadri; HEG, PCBL entering | Epsilon 2,000 t (~2 GWh) → 30,000 t by 2028; Himadri 200 t (Apr 2026)
Electrolyte salt | LiPF₆ | ~0.6-0.8 kg electrolyte | GFCL, Neogen | GFCL commercial since Dec 2025; Neogen developing (Morita JV)
Solvents, additives | EC, DMC, EMC; VC, FEC | In electrolyte | Alkyl Amines, Balaji Amines, Acutaas | Supplying
Separator | PE/PP film, ceramic coated | Thin film | None at scale | Imported
Aluminium foil | Al, ~10-15 µm (cathode side) | ~0.25 kg | Hindalco | Sambalpur, commissioned Jan 2026; supports ~100 GWh
Copper foil | Cu, ~6-8 µm (anode side) | ~0.5 kg | None at scale | Imported
Binder | PVDF (cathode), CMC/SBR (anode) | Small | GFCL (PVDF) | Nearing qualification
Indian LFP cell makers relevant to BESS
Company | Location | Capacity | Status
Ola Cell Technologies | Krishnagiri, TN | 2.5 GWh operating | Only commercial cell producer; 46100 LFP cell BIS-certified
Exide Energy Solutions | Bengaluru, KA | 6 GWh Ph-I (3 GWh LFP prismatic) | Commissioned 23 Sep 2026; SVOLT licence
Reliance New Energy | Jamnagar, GJ | 40 GWh Ph-1 → 120 GWh | LFP / BESS focus; equipment delivered
Waaree Energies | Rambili, AP | 16 GWh integrated (₹8,175 cr) | Cells, packs and BESS; announced Feb 2026
*Typical industry ranges, not from a single source.
Source: [43] BusinessToday (22 Oct 2026); [44] GFCL investor presentation (May 2026); [45] Indian Chemical News (Hindalco); [46] Indian Chemical News (Epsilon); [48] Energetica India (solvents); [9] IEEFA-JMK Jun 2026 (Ola BIS); [50] ICICI Direct (Exide); [51] pv magazine India (Reliance); [52] Mercom (Waaree)

## Slide 8: Investment in BESS tenders and projects in India
Recent awards add ~₹3,500-4,200 cr of standalone BESS capex; government VGF commits ₹9,160 cr for 43.2 GWh
Recent BESS tender awards
Tender | Winner | Capacity won | Tariff discovered | Est. capex*
WBSEDCL 500 MW / 2,000 MWh (Aug 2026) | NTPC Green Energy | 200 MW (~800 MWh) | ₹4.35 lakh/MW/month | ~₹1,000-1,200 cr
WBSEDCL 500 MW / 2,000 MWh (Aug 2026) | Jupiter Wagons | 100 MW (~400 MWh) | Not available | ~₹500-600 cr
GUVNL 450 MW / 900 MWh (Aug 2026) | NLC India Renewables | 275 MW (550 MWh) | ₹2.32 lakh/MW/month | ~₹690-825 cr
GUVNL 450 MW / 900 MWh (Aug 2026) | Sun Drops Energia | 175 MW (350 MWh) | ₹2.32 lakh/MW/month | ~₹440-525 cr
GUVNL 335 MW / 670 MWh (Feb 2026) | Advait, Sun Drops, Equentia | 335 MW (670 MWh) total | ₹2.10-2.12 lakh/MW/month | ~₹840-1,005 cr
SECI 1,500 MW / 6,000 MWh FDRE (Aug 2026) | Waaree 700 MW; NTPC REL 500 MW; ACME 300 MW | 1,500 MW | ₹5.99-6.00/kWh | Not estimated (hybrid)
Company investments, orders and financing
Company | Investment / order | Storage linked
Adani Green | Single-site Khavda BESS; >10 GWh planned in FY27, 50 GWh in 5 years | 1,126 MW / 3,530 MWh
ACME Solar | ₹1,571 cr loan from IIFCL | 300 MW / 1,350 MWh
JSW Energy | ₹443.74 cr BESS + PCS order (Bondada); 40 GWh storage target by 2030 | 200 MW / 400 MWh; 3.2 GWh BESS locked in
NTPC REL / NTPC Green | ₹1,338 cr EPC to Bondada (Sitapur, UP); 17,500 MWh BESS EPC tenders | 50 MW / 200 MWh (+250 MW solar)
AMPIN Energy Transition | ₹1,861.67 cr debt from SMBC and Rabobank | 100 MW hybrid with storage
Government (VGF) | ₹3,760 cr (tranche 1) + ₹5,400 cr (tranche 2) | 13.2 GWh + 30 GWh
*Own calculation at ₹1.25-1.5 cr per MWh installed (₹2.5-3 cr for a 1 MW / 2 MWh utility project). Sector-wide: CareEdge sees >₹4 lakh cr storage investment over 6 years; Rubix up to ₹4.79 lakh cr by FY32.
Source: [8] IEEFA-JMK EnergyWatts Sep 2026 (awards, ACME, AMPIN); [9] IEEFA-JMK Jun 2026 (GUVNL Feb 2026, NTPC REL-Bondada); [23] pv magazine India (JSW); [26] Mercom (Adani); [25] Energy-Storage.news (Adani plans); [33] TaiyangNews (NTPC Green); [2] SolarQuarter (VGF); [3] CareEdge; [5] Rubix; [53] IEEFA-JMK benchmarks

## Slide 9: Companies installing BESS in India: installed and in progress
Adani and ACME together account for about 7 GWh of the ~9.6 GWh operating; a large pipeline sits with NTPC, JSW, Tata Power and IndiGrid
Company | Installed (operational) | In progress / awarded | Main sites
Adani Green Energy | ~3.37 GWh at Khavda (May 2026) | 1,126 MW / 3,530 MWh single-site project; >10 GWh planned in FY27 | Khavda, Gujarat
ACME Solar | ~3.83 GWh cumulative (Aug 2026) | 250 MW / 1,069 MWh FDRE (Ph-I 223 MWh done Oct 2026); 300 MW / 1,350 MWh financed | Bikaner, Jaisalmer, Phalodi, Chittorgarh (RJ)
GEON (Kabra Extrusiontechnik) | 2.88 GWh integrated and commissioned (integrator; client not named) | – | Khavda, Gujarat
Tata Power | 120 MWh with 100 MW solar (Chhattisgarh); 115 MWh FDRE (RJ, Aug 2026); Delhi BESS | 30 MW / 120 MWh Kerala (Areacode); 100 MW across 10 Mumbai sites | CG, RJ, KL, MH, DL
IndiGrid | 180 MW / 360 MWh (GUVNL, May 2026); 20 MW / 40 MWh Kilokari with BRPL (2025) | 250 MW / 500 MWh for NVVN (Bhadla / Banaskantha) | Gujarat, Delhi, Rajasthan
Serentica Renewables | 200 MWh FDRE (Aug 2026) | – | Rajasthan
JSW Energy | Not disclosed | 3.2 GWh BESS locked in: 125 MW / 500 MWh Kerala (SECI-KSEB), 250 MW / 500 MWh Rajasthan (RVUNL) | Kerala, Rajasthan
NTPC / NTPC Green | Not disclosed | 17,500 MWh EPC tenders (Bikaner 7.8, Fatehgarh 3.2, Khavda 6.5 GWh); 200 MW WBSEDCL award | RJ, GJ, WB
Pace Digitek | Manufacturer; 1.25 GWh built | 250 MW / 500 MWh for KPTCL | Karnataka
ReNew | – | 2,000 MWh hybrid BESS | Anantapur, AP
India total | ~9.6 GWh operational (Aug 2026) | ~151 GWh tendered; ~54 GW awarded pipeline | Mostly Rajasthan and Gujarat
Source: [25] Energy-Storage.news (Adani); [26] Mercom (Adani project); [8] IEEFA-JMK Sep 2026 (ACME, Tata, Serentica, totals); [28] BusinessToday (ACME Ph-I); [27] Energetica India (GEON); [31] Tata.com; [29] pv magazine India (IndiGrid); [30] Global Energy Alliance (Kilokari); [23] pv magazine India (JSW); [32] Black Ridge Research; [33] TaiyangNews (NTPC); [22] ESS News (Pace)

## Slide 10: Smaller BESS units: who sells them, including auto OEMs
Auto OEMs reuse their EV cells, pack lines, apps and dealer networks to sell home and commercial batteries, often bundled with solar or an EV
Company | Type | Product and size | Price | How it is sold
Ola Electric | Indian 2W EV OEM | Ola Shakti home BESS: 1.5 / 3 / 5.2 / 9.1 kWh (Oct 2025) | ₹29,999 - ₹1,59,999 (intro, first 10,000) | Own 4680 'Bharat' cells; 4,000+ Ola stores; ₹999 reservation; deliveries from Jan 2026
Ola Electric | Indian 2W EV OEM | Shakti Gen2 4.6 / 9.2 kWh; C&I racks 38-257 kWh; Mahashakti 6.26 MWh (Aug 2026) | ₹99,999 / ₹1,74,999 (home) | LFP cell-to-pack in-house; app monitoring; MoU with Axis Energy for up to 20 GWh by 2032
Tata AutoComp–Gotion | Auto component JV (Tata group) | BESS packs and containers from 6 GWh Pune plant | Not disclosed | Captive: supplies group utility Tata Power
Tesla | Global EV OEM | Powerwall 13.5 kWh (home); Megapack (utility) | Not given here | Own energy business; #1 integrator, 46.7 GWh deployed in 2025
General Motors (GM Energy) | Global auto OEM | PowerBank 10.6 / 17.7 kWh (stack to 35.4 kWh) | Bundles from US$12,700 | Only with EV vehicle-to-home (V2H) bundles, US
BYD | EV and battery OEM | Cells and storage systems, vertically integrated | Not given here | #1 BESS system shipper in 2025 (Benchmark)
Amara Raja | Indian battery maker | Telecom storage | – | >1 GWh telecom storage deployed
Luminous, Exide, Okaya, Loom Solar, Su-Kam | Indian inverter / battery brands | Home and small-commercial lithium storage | – | Dealer networks, sold with home inverters and rooftop solar
Ornate Solar | Indian solar company | Unity Aura C&I cabinet 100-225 kWh | – | Direct to commercial and industrial sites
No Indian four-wheeler OEM (Tata Motors, Mahindra, Maruti, Hyundai) sells a branded home BESS yet; Tata's presence is through Tata AutoComp and Tata Power.
Source: [38] Outlook Business (Ola Shakti, Oct 2025); [39] Upstox (Ola Gen2 portfolio, Aug 2026); [24] Energy-Storage.news (Tata AutoComp-Gotion); [31] Tata.com; [16] Benchmark (Tesla, BYD); [40] Green Car Reports (GM PowerBank); [42] GreentechLead (Amara Raja); [41] Ornate Solar (Indian brands)

## Slide 11: Location of major BESS projects in India
Operational storage is clustered in Rajasthan and Gujarat solar zones; new projects are spreading to substations in the south and east
# | Location | Developer | Capacity | Status
1 | Khavda RE Park, GJ | Adani Green (GEON integrated 2.88 GWh) | ~3.37 GWh; 1,126 MW / 3,530 MWh | Operational
2 | Gujarat (GUVNL) | IndiGrid–EnerGrid | 180 MW / 360 MWh | Operational
3 | Kilokari, Delhi | BRPL with IndiGrid, AmpereHour | 20 MW / 40 MWh | Operational
4 | Rawatbhata, Chittorgarh, RJ | ACME Solar | 223 MWh (Ph-I of 1,069 MWh) | Operational
5 | Jaisalmer, RJ | ACME Solar | 120 MW / 240 MWh | Operational
6 | Phalodi–Jodhpur, RJ | ACME Solar | 33 MW / 120 MWh | Operational
7 | Chhattisgarh | Tata Power (SECI) | 100 MW solar + 120 MWh | Operational
8 | Bikaner, RJ | NTPC REL (EPC tender) | 7,800 MWh | Tendered
9 | Khavda, GJ | NTPC REL (EPC tender) | 6,500 MWh | Tendered
10 | Areacode, Kerala | Tata Power (NHPC for KSEB) | 30 MW / 120 MWh | Under construction
11 | Mylatti, Kerala | JSW Energy (SECI-KSEB) | 125 MW / 500 MWh | Under construction
12 | 6 substations, Odisha | SECI for GRIDCO | 125 MW / 500 MWh | Tendered
13 | Karnataka (KPTCL) | Pace Digitek | 250 MW / 500 MWh | Under construction
14 | Anantapur, AP | ReNew | 2,000 MWh | Under development
15 | Sitapur, UP | NTPC REL (Bondada EPC) | 50 MW / 200 MWh | Under construction
16 | Mumbai (10 sites) | Tata Power | 100 MW | Under construction
Source: [25][26] Adani; [27] GEON; [29] IndiGrid; [30] Kilokari; [28] ACME Ph-I; [9] IEEFA-JMK Jun 2026 (ACME Jaisalmer, Phalodi; Sitapur); [31] Tata Power; [33] NTPC Green EPC; [34] SECI-GRIDCO RfS; [32] Black Ridge Research (Kerala, Karnataka, Anantapur). Map: state boundaries from DataMeet (open data); points are approximate

## Slide 12: Government BESS tender specifications
Three tender types side by side: a VGF-backed build-own-operate tender, a short-term capacity tender and an NTPC EPC tender
Parameter | SECI for GRIDCO: 125 MW / 500 MWh (VGF, BOO) | SECI: 50 MW / 100 MWh (short-term) | NTPC Green: 17,500 MWh (EPC)
Size / duration | 6 projects (5 × 20 MW / 80 MWh + 25 MW / 100 MWh); 4 hours | 50 MW / 100 MWh; 2 hours | Blocks of 200-550 MW; 3-4 hours
Model and term | Build-own-operate; 15-year BESPA | Capacity service; 1-year ESPA (Nov 2026 - Oct 2027) | Turnkey EPC + 15 years O&M; 25-year design life
Location / grid | Inside 6 STU substations; 33 kV underground cable | Existing ISTS-connected, already commissioned plants | At NTPC solar plants; 33 kV
Cycles | 1-2 per day; max 420 per year | 1-2 per day; max 485 in contract | Cells rated ≥10,000 cycles
Availability | ≥95% a year; shortfall LD = 2× capacity charge | ≥95% a year; LD = 2× capacity charge | ≥92% dispatchable at POI over 15 years
Round-trip efficiency | ≥85% AC-AC monthly; no tariff below 70% | ≥85%; ₹3.50/kWh on excess loss; no tariff below 70% | Auxiliary and losses counted in deliverable capacity
Degradation | Min. energy 97.5% (Y1), 87.5% (Y5), 75% (Y10), 62.5% (Y15); augmentation at developer cost | – | 100% at COD, 95% after Y1, ≥92% at handover
VGF | Up to ₹18 lakh/MWh: 20% at financial close, 50% at COD, 30% a year later | None | –
Timeline | Commissioning 18 months; financial close 6 months | Must be operating at bid date | Bids closed 25 Jun 2026
Bank guarantees | EMD ₹9 lakh/MW; PBG ₹22.5 lakh/MW | EMD ₹2.4 cr; PBG ₹6 cr | –
Local content | EMS software developed in India; no refurbished cells | – | –
Rules that apply to all grid BESS
CEA Safety Amendment 2026 (from 1 Apr 2027) | CEA Technical Standards 2026 | VGF domestic content (Dec 2025)
Two-fault tolerance, automatic fire suppression in every container, explosion protection, third-party fire audit | Grid-forming and black start for ≥50 MW; capacity retention ≥90% / 80% / 70% at 5 / 10 / 15 years | ≥20% of procurement cost local; EMS counts
Source: [34] SECI RfS for GRIDCO (RfS No. SECI/C&P/IPP/15/0015/25-26); [35] SolarQuarter (SECI 50 MW / 100 MWh, Aug 2026); [33] TaiyangNews (NTPC Green EPC); [36] Energetica India (CEA safety rules); [37] SolarQuarter (CEA technical standards); [15] Energy-Storage.news (20% DCR)

## Slide 13: Sources (1 of 2)
[1] SolarQuarter – Govt roadmap to build 60.63 GW storage by FY30 (Feb 2026)
https://solarquarter.com/2026/02/04/government-unveils-multi-pronged-policy-financial-and-regulatory-roadmap-to-build-60-63-gw-energy-storage-capacity-by-fy30/
[2] SolarQuarter – ₹5,400 cr VGF and transmission incentives (Aug 2026)
https://solarquarter.com/2026/08/12/india-strengthens-energy-storage-framework-with-inr-5400-crore-vgf-and-transmission-incentives/
[3] NewKerala / ANI – Storage requirement to reach 411 GWh by FY32 (CareEdge)
https://www.newkerala.com/news/a/indias-energy-storage-requirement-reach-411-gwh-fy32-434.htm
[4] TaiyangNews – India curtails 1.46 billion units of solar in 2 months
https://taiyangnews.info/markets/india-curtails-146-billion-units-solar-power-2-months
[5] pv magazine India – BESS requirement 236 GWh by FY32 (Rubix, Oct 2026)
https://www.pv-magazine-india.com/2026/10/07/indias-battery-energy-storage-system-requirement-to-rise-nearly-seven-fold-to-236-gwh-by-fy2031-32-rubix-data-sciences/
[6] Angel One – Storage requirement 888 GWh by 2035-36 (IESA)
https://www.angelone.in/news/economy/india-s-energy-storage-requirement-to-reach-888-gwh-by-2035-36-report
[7] ESS News – India adds 8.2 GWh BESS in H1 2026 (Mercom)
https://www.ess-news.com/2026/09/14/india-adds-8-2-gwh-of-new-bess-capacity-in-h1-2026/
[8] IEEFA-JMK – EnergyWatts September 2026
https://ieefa.org/sites/default/files/2026-09/ESSjmk-0926.pdf
[9] IEEFA-JMK – EnergyWatts June 2026
https://ieefa.org/sites/default/files/2026-08/ESSjmk-0626.pdf
[10] JMK Research – EnergyWatts September 2026
https://jmkresearch.com/?p=139948
[11] Energetica India – India adds 3.69 GW RE in Sep 2026
https://www.energetica-india.net/news/india-adds-3-69-gw-re-capacity-in-september-2026-total-addition-in-fy27-reaches-24-56-gw
[12] pv magazine India – Record 45 GW solar in FY2026 (JMK)
https://www.pv-magazine-india.com/2026/04/10/india-installs-record-45-gw-solar-capacity-in-fy2026
[13] MNRE – Physical progress (year-end installed RE capacity)
https://mnre.gov.in/physical-progress/
[14] Renewable Watch – RPO and ESO up to 2030 notified by MoP
https://renewablewatch.in/2022/07/25/rpo-and-eso-upto-2030-notified-by-the-ministry-of-power/
[15] Energy-Storage.news – 20% domestic content rule for BESS VGF
https://www.energy-storage.news/?p=92648
[16] Benchmark Mineral Intelligence – Top storage cell suppliers and integrators 2025
https://source.benchmarkminerals.com/article/the-top-energy-storage-cell-suppliers-and-system-integrators-in-2025
[17] SolarQuarter – Chinese companies capture 76% of BESS integrator market (Wood Mackenzie)
https://solarquarter.com/2026/07/02/chinese-companies-capture-76-of-global-bess-integrator-market-in-2025-wood-mackenzie-reports/
[18] ESS News – InfoLink: 2025 storage cell shipments 612 GWh
https://www.ess-news.com/2026/02/09/infolink-2025-energy-storage-cell-shipments-jump-95-to-612-gwh-as-market-flips-from-glut-to-tightness/
[19] pv magazine USA – BloombergNEF: energy storage reaches the 100 GW era
https://pv-magazine-usa.com/2026/05/11/bloombergnef-confirms-energy-storage-has-reached-the-100-gw-era
[20] Energetica India – From imports to integration: BESS manufacturing
https://www.energetica-india.net/news/from-imports-to-integration-is-india-ready-to-manufacture-bess-at-scale
[21] Renewable Watch – Waaree ESS commissions 5.15 GWh facility
https://renewablewatch.in/2026/07/17/waaree-ess-commissions-5-15-gwh-bess-container-manufacturing-facility/
[22] ESS News – Pace Digitek builds 1.25 GWh of BESS in first year
https://www.ess-news.com/2026/07/09/indias-pace-digitek-manufactures-more-than-1-25-gwh-of-bess-capacity-in-first-year-of-operation/
[23] pv magazine India – JSW Energy secures 200 MW / 400 MWh BESS order
http://www.pv-magazine-india.com/2026/07/13/jsw-energy-secures-200-mw-400-mwh-bess-order-from-bondada-renewable-energy/
[24] Energy-Storage.news – Tata AutoComp-Gotion JV supplies first BESS units
https://www.energy-storage.news/tata-autocomp-gotion-jv-supplies-first-bess-units-to-tata-power-project-in-pune-india/
[25] Energy-Storage.news – Adani Green reaches 3.37 GWh BESS at Khavda
https://www.energy-storage.news/?p=101940
[26] Mercom India – Adani enters BESS with 1,126 MW / 3,530 MWh project
https://www.mercomindia.com/adani-group-enters-bess-sector-with-1126-mw-3530-mwh-project-at-khavda
[27] Energetica India – GEON commissions 2.88 GWh BESS at Khavda
https://www.energetica-india.net/news/geon-commissions-288-gwh-bess-project-at-khavda-marking-major-milestone-in-indias-energy-storage-sector
[28] BusinessToday – ACME Solar commissions Phase-I BESS in Rajasthan
https://www.businesstoday.in/markets/stocks/story/acme-solar-in-focus-after-commissioning-phase-i-bess-project-in-rajasthan-558935-2026-10-01

## Slide 14: Sources (2 of 2)
[29] pv magazine India – IndiGrid commissions 180 MW / 360 MWh BESS
http://www.pv-magazine-india.com/2026/05/11/indigrid-commissions-180-mw-360-mwh-battery-energy-storage-system-project-in-gujarat/
[30] Global Energy Alliance – India's first utility-scale standalone BESS (Kilokari)
https://energyalliance.org/india-first-utility-scale-standalone-battery-energy-storage-system/
[31] Tata.com – Tata Power: leading the battery storage charge
https://www.tata.com/newsroom/business/tata-power-battery-storage
[32] Black Ridge Research – Largest BESS projects in India 2026
https://www.blackridgeresearch.com/blog/list-of-largest-upcoming-ongoing-battery-energy-storage-bess-projects-india
[33] TaiyangNews – NTPC Green launches 17,500 MWh BESS EPC tenders
https://taiyangnews.info/tenders/ntpc-green-launches-17500-mwh-bess-epc-tenders
[34] SECI – RfS for 125 MW / 500 MWh BESS for GRIDCO
https://www.seci.co.in/uploads/tenders/RfS-BESS_Projects-GRIDCO.pdf
[35] SolarQuarter – SECI invites bids for 50 MW / 100 MWh standalone ESS
https://solarquarter.com/2026/08/29/seci-invites-bids-for-50-mw-100-mwh-standalone-energy-storage-system/
[36] Energetica India – CEA issues 2026 BESS safety rules
https://www.energetica-india.net/news/cea-issues-2026-bess-safety-rules-mandates-two-fault-tolerance-and-fire-audits-from-april-2027
[37] SolarQuarter – CEA 2026 technical standards for BESS
https://solarquarter.com/2026/04/14/cea-2026-amendment-sets-new-technical-standards-for-bess-solar-and-wind-projects-in-india/
[38] Outlook Business – Ola launches Ola Shakti residential BESS
https://www.outlookbusiness.com/news/ola-launches-ola-shakti-enters-indias-residential-bess-market-with-4680-bharat-cells
[39] Upstox – Ola Electric unveils home-to-grid storage portfolio
https://upstox.com/news/business-news/latest-updates/ola-electric-unveils-home-to-grid-battery-storage-portforlio-starting-at-99-999/article-198754/
[40] Green Car Reports – GM PowerBank home energy storage
https://www.greencarreports.com/news/1144702_gm-powerbank-home-energy-storage-arrives-could-outflex-tesla
[41] Ornate Solar – Top 10 BESS manufacturers in India
https://ornatesolar.com/blog/top-10-battery-energy-storage-system-bess-manufacturers-in-india
[42] GreentechLead – India EV and battery investments 2026 (Amara Raja)
https://greentechlead.com/electric-vehicle/india-ev-and-battery-investments-2026-tata-amara-raja-and-exide-expand-gigafactory-plans-55902
[43] BusinessToday – India has failed to build a battery cell ecosystem (22 Oct 2026)
https://www.businesstoday.in/auto/story/bt-big-story-india-has-failed-to-build-an-ecosystem-of-battery-cells-can-a-new-pli-change-this-562898-2026-10-22
[44] Gujarat Fluorochemicals – Investor presentation (May 2026)
https://nsearchives.nseindia.com/corporate/FLUOROCHEM_26052026164956_GFCL_Investor_Presentation_26May2026.pdf
[45] Indian Chemical News – Hindalco commissions battery foil facility
https://www.indianchemicalnews.com/battery/lite/hindalco-to-invest-rs-21000-crore-on-smelter-expansion-commissions-frp-and-battery-foil-facilities-in-odisha-29082
[46] Indian Chemical News – Interview: Vikram Handa, Epsilon Group
https://www.indianchemicalnews.com/interviews/india-must-act-now-to-dominate-global-battery-materials-vikram-handa-managing-director-epsilon-group-581
[47] pv magazine – Chinese makers scale from 314 Ah to 500 Ah+ LFP cells
https://www.pv-magazine.com/2026/01/23/chinese-battery-makers-scale-up-from-314ah-to-500ah-plus-lfp-cells/
[48] Energetica India – Alternative battery supply chain (electrolyte solvents)
https://www.energetica-india.net/articles/indias-growing-dominance-in-the-ev-sector-a-global-shift-towards-an-alternative-supply-chain
[49] Energetica India – Waaree ESS commissions 5.15 GWh facility
https://www.energetica-india.net/news/waaree-ess-commissions-515-gwh-bess-container-manufacturing-facility
[50] ICICI Direct – Exide commissions Phase-I of 6 GWh cell plant
https://www.icicidirect.com/research/equity/trending-news/exide-arm-commissions-phase-i-of-6-gwh-li-ion-cell-plant-in-bengaluru
[51] pv magazine India – Reliance targets 120 GWh BESS and cell capacity
https://www.pv-magazine-india.com/2026/06/22/reliance-targets-120-gwh-of-annual-bess-and-cell-manufacturing-capacity-first-phase-to-start-production-this-year/
[52] Mercom India – Waaree to set up 16 GWh gigafactory in Andhra Pradesh
https://www.mercomindia.com/waaree-to-set-up-16-gwh-lithium-ion-battery-gigafactory-in-andhra-pradesh
[53] SolarQuarter – SECI 50 MW / 100 MWh (RTE, availability benchmarks); India_BESS_Benchmarks_Oct2026.docx (ev repo)
https://solarquarter.com/2026/08/29/seci-invites-bids-for-50-mw-100-mwh-standalone-energy-storage-system/
[54] BESS Deep Research Report, Oct 2026 – ev repo (Crypto-ashish/ev)
https://github.com/Crypto-ashish/ev/blob/main/BESS_Deep_Research_Report_Oct2026.docx
[55] EV SIM.pptx – project reference deck (Generation 3 slide)
Project file