## Slide 1: How a BESS charges from the grid and discharges back to it
Midday: surplus solar is stored as DC in the cells. Evening: the same path runs in reverse to feed the peak
1. Charging
(midday)
Solar / grid
Surplus AC power at 33 kV
Transformer
Steps voltage down to ~0.6-0.8 kV
PCS (rectifier)
Converts AC → DC
Racks + BMS
~1,280 V DC; BMS limits current and voltage
Cells store
Li⁺ moves cathode → graphite anode
2. Discharging
(evening peak)
Cells release
Li⁺ moves back to cathode; e⁻ flow out
Racks + BMS
DC out; BMS stops at low SOC
PCS (inverter)
Converts DC → AC at 50 Hz, synced to grid
Transformer
Steps voltage up to 11-33 kV
Grid / DISCOM
Power reaches homes and industry
Same equipment both ways: the PCS works as a rectifier while charging and as an inverter while discharging.
Charging vs discharging
Item | Charging | Discharging
When | Midday, when solar is surplus and power is cheap | Evening peak after sunset
Who decides | EMS follows SLDC / DISCOM schedule | EMS follows SLDC / DISCOM schedule
Inside the cell | LiFePO₄ → FePO₄ + Li⁺ + e⁻ ; Li⁺ goes into graphite (LiC₆) | LiC₆ → 6C + Li⁺ + e⁻ ; Li⁺ returns to FePO₄
BMS stops at | Upper voltage limit (~3.65 V per cell) or full SOC | Lower voltage limit (~2.5-2.8 V per cell) or minimum SOC
Example: 1 MW / 2 MWh | Draws ~2.35 MWh over ~2-2.5 hours | Delivers 2 MWh over 2 hours at 1 MW
Losses | ~15% lost in PCS, transformer, cells and cooling (tenders require ≥85% round-trip efficiency) | 
Source: [1] BESS Deep Research Report (ev repo, sections 4.1, 5.3, 11.6); [2] SolarQuarter – SECI 50 MW / 100 MWh tender (≥85% AC-to-AC RTE). Example energy is own calculation: 2 MWh ÷ 0.85 ≈ 2.35 MWh.

## Slide 2: Sources
[1] BESS Deep Research Report, Oct 2026 – ev repo (Crypto-ashish/ev)
https://github.com/Crypto-ashish/ev/blob/main/BESS_Deep_Research_Report_Oct2026.docx
[2] SolarQuarter – SECI invites bids for 50 MW / 100 MWh standalone energy storage system (Aug 2026)
https://solarquarter.com/2026/08/29/seci-invites-bids-for-50-mw-100-mwh-standalone-energy-storage-system/